## Equipment Category P
Fault Type | Inspection | H2 | CH4 | C2H2 | C2H4 | C2H6 | CO | CO2 | Ref
D1 | Loosening of potential ring on bushing, with marks of sparking/tracking | 78 | 20 | 28 | 13 | 11 | 440 | 784 | 2
D1 | Selector breaking current in selector tank | 305 | 100 | 541 | 161 | 33 | 200 | 3700 | 3
D1 | Tracking to HV bushing | 1230 | 163 | 692 | 233 | 27 | 130 | 115 | 4
D1 | Tracking in bushing | 645 | 86 | 317 | 110 | 13 | 74 | 114 | 4
D1 | Sparking on tank walls to the bushing | 95 | 10 | 39 | 11 |  | 122 | 467 | 4
D1 | Low energy arcing on bushing | 595 | 80 | 244 | 89 | 9 | 524 | 2100 | 14
D1 | Sparking from core to ground | 1330 | 10 | 182 | 66 | 20 | 231 | 1820 | 14
D2 | Flashover from LV to ground, external | 440 | 89 | 757 | 304 | 19 | 299 | 1190 | 4
D2 | Short circuit from LV to connector | 545 | 130 | 239 | 153 | 16 | 660 | 2850 | 4
D2 | Arcing from windings to porcelain | 7150 | 1440 | 1760 | 1210 | 97 | 608 | 2260 | 4
D2 | Short circuit in windings | 755 | 229 | 460 | 404 | 32 | 845 | 5580 | 4
D2 | Bushing swollen, tank opened | 1570 | 1110 | 1830 | 1780 | 175 | 135 | 602 | 4
D2 | Arcing to magnetic circuit (ground) | 3090 | 5020 | 2540 | 3800 | 323 | 270 | 400 | 4
D2 | Short circuit between conductors | 1820 | 405 | 634 | 365 | 35 | 1010 | 8610 | 4
D2 | Arcing in windings | 260 | 215 | 277 | 334 | 35 | 130 | 416 | 14
D2 | Arcing in windings | 75 | 15 | 26 | 14 | 7 | 105 | 322 | 14
D2 | Arcing in oil | 60 | 5 | 21 | 21 | 2 | 188 | 2510 | 14
D2 | Arcing from bushing to tank | 1500 | 395 | 323 | 395 | 28 | 365 | 576 | 14
D2 | Arcing from windings to core | 20000 | 13000 | 57000 | 29000 | 1850 | 2600 | 2430 | 14
D2 | Arcing in oil (turret) | 3700 | 1690 | 3270 | 2810 | 128 | 22 | 86 | 14
D2 | Arcing in oil (turret) | 2770 | 660 | 763 | 712 | 54 | 522 | 1490 | 14
D2 | Arcing from HV to tank | 1170 | 255 | 325 | 312 | 18 | 5 | 1800 | 14
T1/T2 | High circulating currents between conductors with winding damage | 1270 | 3450 | 8 | 1390 | 520 | 483 | 44500 | 3
T1/T2 | Circulating currents in LV windings and core | 3420 | 7870 | 33 | 6990 | 1500 | 573 | 4640 | 3
T1/T2 | Vertical bar buses burnt out, carbonization of paper strips | 48 | 610 |  | 10 | 29 | 1900 | 970 | 10
T1/T2 | Carbonized windings during heat run tests | 12 | 18 |  | 4 | 4 | 559 | 1710 | 12
T1/T2 | Circulating currents in magnetic tank shunt during heat run tests | 66 | 60 |  | 7 | 2 | 76 | 90 | 12
T1/T2 | Overheating of conductor < 200 °C | 14 | 44 | 1 | 7 | 124 | 128 | 2746 | 16
T3 | Hot spot at connection | 8800 | 64064 |  | 95650 | 72128 | 290 | 90300 | 1
T3 | Circulating currents between yoke clamps and connecting bolts | 6709 | 10500 | 750 | 17700 | 1400 | 290 | 1500 | 3
T3 | Steel lamination eroded | 290 | 966 | 57 | 1810 | 299 | 72 | 756 | 4
T3 | Circulating currents in clamping bolt | 2500 | 10500 | 6 | 13500 | 4790 | 530 | 2310 | 4
T3 | High contact resistance of winding terminal | 400 | 940 | 24 | 210 | 820 | 390 | 1700 | 10
T3 | Ground wiring burnt and ruptured by circulating current | 6 | 2990 | 67 | 29990 | 26076 | 6 | 26 | 10
T3 | Bad contact in windings | 290 | 1260 | 8 | 820 | 231 | 228 | 826 | 14
T3 | Burnt lamination during heat run test | 107 | 143 | 2 | 222 | 34 | 193 | 1330 | 14